## Inputs
Instructions
Fill out inputs in order from top to bottom. If you change one, make sure to re-verify all the inputs below the change | must enter input |  | Eligibility Requirements for all projects
The installation of the GSHP should meet the following design parameters to ensure a properly sized circulation pump.
| default value - use actual value if known |  | • Circulation pump is included in the manufacturer assembly of the GSHP system Or; • Circulation pump flow rate less than or equal to 3.0 GPM per system ton
deemed value
• Variable flow controls on pumps serving systems greater than 10 tons. Variable flow controls include one of the following: o A variable speed system pump controlled from differential pressure and 2-way water flow control valves on each heat pump. o Individual on/off pumps on each heat pump controlled by heat pump demand. The heat pumps may be decoupled from the ground heat exchanger using a separate variable speed pump controlled by differential temperature across the ground loop.
This tool does not yet calculate savings from DHW - some inputs not needed
Use Case
Utility type | -Choose One-
Program Type | -Choose One-
Verify the project meets eligibility requirements to right- review carefully | -Choose One- |  | • On/off or variable flow controls on pumps for systems less than 10 tons. On/off pump controls shall operate only when heat pump(s) are running.
STOP here - this tool does not calculate savings for ineligible projects
• System pumping head less than 80 feet. For systems 10 tons or smaller system pumping head should not exceed 40 feet.
Eligibility Requirements - specific to Program Type
Existing Heating Fuel | -Choose One- |  |  | Select Program Type from the pulldown menu to the left
Use Case Chosen:
Inputs Incomplete
Select Program Type from the pulldown menu to the left
Site Information
Building Type | -Choose One-
Climate Zone | -Climate Zone-
Select Program Type from the pulldown menu to the left
Existing Cooling System Information, If Applicable
System Type | System Subtype | EERExist
-System Type- | -System subtype- | 0
Energy Efficiency Ratio (EER) of existing cooling unit. In (kBtu/hr/kW). Use actual EER rating where it is possible to measure or reasonably estimate. If it is not possible to estimate existing unit efficiency, change project to Time-of-Sale. If EER unknown but SEER is available, convert using the tool to the right*
Select Program Type from the pulldown menu to the left
SEER-to-EER Calculator tool
|  |  |  | Known SEER | 0 | 0 | Calculated EER
Existing Electric Heating System Inputs, If Applicable
System Type | System Subtype |  | Incomplete
-Existing Electric System Type- | -System subtype- |  | 0
-Existing Gas System Type- | -System Subtype- |  | 0%
Incomplete Inputs
System Information - Required Inputs - Pay careful attention to the units
Variable | Value | Default value | Units | Definition
Capacitycool | 0 | Required Input | (Btu/hr) | Cooling Capacity of Ground Source Heat Pump. Actual installed
EERGSHP | 0 | Required Input | (kBtu/hr / kW) | Part Load Energy Efficiency Ratio efficiency of efficient GSHP unit. Actual installed
CapacityHeat | 0 | Required Input | (Btu/hr) | Heating Capacity of Ground Source Heat Pump. Actual installed
COPGSHP | 0 | Required Input | (unitless) | Part Load Coefficient of Performance of efficient GSHP. Actual installed
ElecDHW | 0 | Tool incomplete | flag | 1 if building has electric DHW. 0 if building has non electric DHW. 0 if one to one replacement of existing Ground Source Heat Pump
%DHW | 0 | Tool incomplete | (%) | Percentage of total DHW load that the GSHP will provide. Actual if known. If unknown and if desuperheater installed assume 44%. 0% if no desuperheater installed
Inputs Completeness Check | [6 empty] | Incentive Qualified for
| Electric cooling savings | Incomplete - Required inputs still needed |  |  |  |  | cooling capacity in tons | 0
| Electric heating savings | Incomplete - Required inputs still needed |  |  |  |  | Incentive rate per ton | 500
| Electric DHW savings | Tool incomplete |  |  |  |  | Eligibility | Ineligible
| Gas heating savings | Not Needed - Not Applicable to this project |  |  |  |  | Total Incentive | 0
| Gas DHW savings | Tool incomplete
Default Values - Only Change if supported with reliable site/system data
Variable | Value | Default value | Units | Definition
EFLHCool | Incomplete | Incomplete | (hours) | Cooling Equivalent Full Load Hours. Dependent on building type, provided in section 4.4 HVAC End Use
EERbase | Incomplete | Incomplete | (kBtu/hr / kW) | Energy Efficiency Ratio (EER) of baseline replacement cooling system. Use minimum standard efficiencies as specified in tables in ‘Definition of Baseline Equipment’ section
ElecHeat | Incomplete | Incomplete | flag | 1 if baseline/existing heating system is electric. 0 if existing system is non electric
EFLHHeat | Incomplete | Incomplete | (hours) | Heating Equivalent Full Load Hours. Dependent on building type, provided in section 4.4 HVAC End Use
HSPFbase | Incomplete Inputs | Incomplete Inputs | (kBtu/kWh) | Heating System Performance Factor of new replacement baseline heating system [of the existing type, but new]
HSPFASHP | Input CapacityHeat | Input CapacityHeat | (kBtu/kWh) | Heating System Performance Factor of new replacement ASHP. (for fuel switch). Refer to applicable Table in ‘Definition of Baseline Equipment’ section
GasEffbase | Incomplete | Incomplete | % | Minimum federal standard baseline efficiency of boiler or furnace
kWhtoTherm | Incomplete | Incomplete | Therm/kWh | Converts source kWh to Therms
Efelecbase |  | Tool incomplete | 0 | Energy Factor of baseline electric DHW. Actual. If unknown or for new construction assume federal standard as defined in applicable table in ‘Definition of Baseline Equipment’ section
HotWaterUseGallon |  | Tool incomplete | oof. Yeesh. Separate sub input routine required | 0
Deemed or Calculated Values - Should not be changed
Variable | Value | Default value | Units | Definition
Constant | 3.412 | 3.412 | (kWh/kbtu) | Constant to convert the COP of the unit to the Heating Season Performance Factor (HSPF)
Gas_Heating_Load | Incomplete | Incomplete | therms | Estimate of annual heating load = Capacityheat * EFLHheat / 100,000
Hgrid | Incomplete | Incomplete | btu/kWh | Heat rate of the grid in btu/kWh… full description in TRM
γWater | 8.33 | 8.33 | (lb/gal) | Density of water. 8.33 pounds per gallon
Tout | 125 | 125 | (°F) | Tank temperature. 125°F
Tin | 54 | 54 | (°F) | Incoming water temperature from well or municiplal system. 54°F
Constant | 1 | 1 | (Btu/lb*°F) | Heat Capacity of water
Constant | 3412 | 3412 | (kWh/btu) | Conversion from Btu to kWh

## Outputs-Savings
Annual Electric Savings - kWh |  | Lifetime
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Total annual electric savings | Incomplete | Incomplete
Mid-Life Adjusted Annual Savings - kWh, If Applicable |  | Lifetime
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Total annual electric savings | Incomplete | Incomplete
Annual Gas Savings - Therms |  | Lifetime
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Total annual gas savings | Incomplete | Incomplete
Mid-Life Adjusted Annual Savings - Therms, If Applicable |  | Lifetime
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Total annual gas savings | Incomplete | Incomplete

## lookups (hidden)
-Choose One-
Gas and Electric (Ameren) | As Per commented, it's possible this means a customer gets gas or electric only from the utility. For now, we assume that because Ameren is gas and electric, all Ameren projects are both regardless of the customer
-Choose One- |  | Variable eligibility requirements (by use case)
Time of Sale |  | New Construction | i. The installation of a new Ground Source Heat Pump system must meet ENERGY STAR efficiency standards presented below in a new C&I building. | ii. Calculation note: Per the TRM, the baseline in this case should be determined via EM&V. The algorithms are provided to allow savings to be calculated from any baseline condition. Documentation should be provided to justify choice of baseline | intentionally blank | intentionally blank
Early Replacement/Retrofit |  | Time of Sale | i. The planned installation of a new Ground Source Heat Pump system must meet ENERGY STAR efficiency standards (see below) to replace an existing system(s) that does not meet the criteria for early replacement (described in section C of the TRM measure and copied below). | ii. Calculation note: The baseline in this case is an equivalent replacement system to that which exists currently in the building. The calculation of savings is dependent on whether an incentive for the installation has been provided by both a gas and electric utility, only an electric utility or only a gas utility. | iii. Calculation note: DHW savings are calculated based upon the fuel type and efficiency of the existing unit. | intentionally blank
New Construction |  | Early Replacement/Retrofit | i. Project includes early removal of functioning electric or gas space heating and/or cooling systems from service, prior to the natural end of life and replacement with a new high efficiency Ground Source Heat Pump system. | ii. Note the baseline in this case is the existing equipment being replaced. The calculation of savings is dependent on whether an incentive for the installation has been provided by both a gas and electric utility, only an electric utility or only a gas utility. DHW savings are calculated based upon the fuel and efficiency of the existing unit. | iii. Early Replacement determination will be based on meeting the following conditions: • The existing unit is operational when replaced, or • The existing unit requires minor repairs to be operational, defined as costing less than: Air Source Heat Pump $263/ton Chiller $308/ton Boiler (Steam) $3.87/ kBtu Boiler (Hot Water) $4.25/ kBtu Furnace $2.49/ kBtu Ground Source Heat Pump $2,185/ton | iv. If the operational status or repair cost of the existing unit is unknown use time of sale assumptions.
|  | -Choose One- | Select Program Type from the pulldown menu to the left | Select Program Type from the pulldown menu to the left | Select Program Type from the pulldown menu to the left | Select Program Type from the pulldown menu to the left
-Choose One-
Meets requirements
Does not meet requirements
Uncertain
-Choose One-
Gas
Electric
Possible Use cases
New construction, non-fuel switch |  | • The existing unit is operational when replaced, or
Time of Sale, non-fuel switch |  | • The existing unit requires minor repairs to be operational, defined as costing less than716: Existing System Maximum repair cost Air Source Heat Pump $263/ton Chiller $308/ton Boiler (Steam) $3.87/ kBtu Boiler (Hot Water) $4.25/ kBtu Furnace $2.49/ kBtu Ground Source Heat Pump $2,185/ton
Early Replacement, non-fuel switch |  | • All other conditions will be considered Time of Sale.
Early Replacement, fuel switch
New construction, fuel switch | I'm really not sure what this case even means, but it's specifically in the TRM. For now it's an option in this tool, but I don't know when it applies
Time of Sale, fuel switch
Inputs Incomplete
Chosen use case
Inputs Incomplete
Required electric inputs
New construction, non-fuel switch
Time of Sale, non-fuel switch
Early Replacement, non-fuel switch
Early Replacement, fuel switch
New construction, fuel switch
Time of Sale, fuel switch
Required gas inputs
New construction, non-fuel switch
Time of Sale, non-fuel switch
Early Replacement, non-fuel switch
Early Replacement, fuel switch
New construction, fuel switch
Time of Sale, fuel switch
-Climate Zone- | Incomplete
Zone 1 (Rockford) | 1
Zone 2 (Chicago) | 2
Zone 3 (Springfield) | 3
Zone 4 (Belleville) | 4
Zone 5 (Marion) | 5
| Air Conditioning |  | Space Heating |  | DHW baseline
-Choose One- | Incomplete |  | Incomplete |  | Incomplete
Time of Sale
Early Replacement/Retrofit
New Construction | Minimum Federal Efficiency ASHP | Table 7 | Minimum Federal Efficiency ASHP | Table 7 | Federal Standard efficiency electric DWH heater | Table 6
Baseline definitions
Early replacement / Retrofit: The baseline for this measure is the efficiency of the existing heating, cooling and hot water equipment for the assumed remaining useful life of the existing unit, and a new baseline heating and cooling system for the remainder of the measure life (as provided in table above).
Time of Sale: The baseline for this measure is a new replacement unit of the same system type as the existing unit, meeting the minimum standard efficiencies provided above.
To calculate savings with an electric baseline, the baseline equipment is assumed to be an Air Source Heat Pump meeting the Federal Standard efficiency level as outlined in Table 2; and a Federal Standard electric hot water heater efficiency level as outlined in Table 6. To calculate savings with a chiller/unitary cooling systems and boiler/furnace baseline, the baseline equipment is assumed to meet the minimum standard efficiencies as outlined in the Table 3 Table for chillers/unitary cooling systems , and Table 4 for boilers or Table 5 for furnaces. If a desuperheater is installed, the domestic hot water heater minimum standard efficiency is calculated as per Table 6 below.
EERbase lookup tables
EERbase | Incomplete |  | I'm assuming the same system type as the existing system and the same capacity of the proposed system. This is not explicitly called out in the TRM, but makes the most sense to me
-Select System Type First- |  |  | could clean up this section and break some of the logic into subcells instead of all in the EERbase cell
-System Type-
Ground water source HP |  | N/A, New Construction
Ground source HP
Air cooled HP (Split or Single package AC)
Air cooled chiller
Water cooled Chiller
Ground water source HP
-System subtype- | EER
Water to air | 18
Water to water | 16.3
Ground source HP
-System subtype- | EER |  |  | water to air | EER | Range
Water to air | separate table |  |  | 0 | Enter system capacity
Brine to air | 14.1 |  |  | 0.1 | 12.2 | <17kBtuh
Water to water | 10.6 |  |  | 17000 | 13 | 17-65kbtuh
Brine to water | 12.1 |  |  | 65000 | 13 | 65-135kBtuh
|  |  |  | 135000 | Verify Large Capacity Baseline
Air cooled HP (Split or Single AC package AC) |  |  |  | Standard air cooled AC | EER | SEER | Range | Rating with ER or no heat | Rating without ER heat |  | These values change whether the existing heat is electric resistance or not
-System subtype- | EER | SEER |  | 0 | Enter system capacity | [5 empty] | ER or other heat?
Standard air cooled AC | separate table |  |  | 0.1 | 11.76 | 14 | <65kBtuh |  |  |  | No
Through-the-wall | 10.56 | 12 |  | 65000 | 10.8 |  | 65-135kButh | 11 | 10.8
Single-duct, high-velocity | 9.9 | 11 |  | 135000 | 10.4 |  | 135-240kBtuh | 10.6 | 10.4
|  |  |  | 240000 | 9.3 |  | 240+kBtuh | 9.5 | 9.3
Air cooled chiller
-System subtype- | EER | type |  |  | Path B IPLV | This is a variable for the tool user/designer. The baseline efficiency for chillers depends on which rating method we think best compares to the way GSHPs are rated. Each path produces different input values for the baseline, which affects the savings. Path B IPLV is most conservative. Path B FL is most savings. There might be a "right" choice, but I don't know
None Needed | 15.8 | Air cooled <150 tons
Water cooled Chiller
-System subtype- | EER | Type |  |  | Positive displacement lookup |  |  | Centrifugal lookup
Postive displacement | #N/A | Enter system capacity |  |  | 0 | Enter system capacity |  | 0 | Enter system capacity
Centrifugal | #N/A | Enter system capacity |  |  | 0.1 | Water cooled, PD <75 tons |  | 0.1 | Water cooled, cetrifugal <150 tons
[5 empty] | 900000 | Water cooled, PD 75-150 tons |  | 1800000 | Water cooled, cetrifugal 150-300 tons
[5 empty] | 1800000 | Water cooled, PD 150-300 tons |  | 3600000 | Water cooled, cetrifugal 300-400 tons
[5 empty] | 3600000 | Water cooled, PD 300-600 tons |  | 4800000 | Water cooled, cetrifugal 400-600 tons
[5 empty] | 7200000 | Water cooled, PD 600+ tons |  | 7200000 | Water cooled, cetrifugal 600+ tons
Electric Heating inputs
Chosen system type | -Existing Electric System Type-
Chosen system sub type | -System subtype-
CapacityHeat | 0 | btu/hr
HSPFbase | Incomplete Inputs | I'm assuming the same system type as the existing system and the same capacity of the proposed system. This is not explicitly called out in the TRM, but makes the most sense to me
HSPHashp | Input CapacityHeat | The TRM says to "refer to the applicable table" without giving further guidance to choose a specific baseline model. I am choosing a single package unit for <65kBtuh becausue it results in conservative savings. For larger units, the test procedure is an input below - starting with a conservative default
-Existing Electric System Type- |  | Select System Type
Not Needed |  | Incomplete Inputs
Not Needed
Not Needed
Not Needed |  | No subsystem needed
[8 empty] | 47F db/43F wb outdoor air |  | This is a variable for the tool user/designer. The baseline efficiency for Air Cooled (heat mode) systems above 65kBtuh depends on which test method we think best compares to the way GSHPs are rated. Each path produces different input values for the baseline, which affects the savings. [47F db/43F wb outdoor air] produces conservative savings; [17F db/15F wb outdoor air] produces higher savings. There might be a "right" choice, but I don't know
Air Source Heat Pump | HSPF |  | Range |  | Split systemHSPF | Single Package HSPF | COP
-System subtype- | Select System Type |  |  | 0 | Input CapacityHeat | Input CapacityHeat
Air cooled HP (heat mode) - Split Package | Input CapacityHeat |  | <65kBtuh | 0.1 | 8.2 | 8
Air cooled HP (heat mode) - Single Package | Input CapacityHeat |  | 65-135kBtuh | 65000 | 11.2596 | 11.2596 | 3.3
Through-the-wall - Split Package | 7.4 |  | >135kBtuh | 135000 | 10.9184 | 10.9184 | 3.2
Through-the-wall - Single Package | 7.4
Small-duct, high-velocity | 6.8 | [7 empty] | 3.412 | This converts COP to HSPF. Per the TRM. I'm not sure its really that easy in practice (or possible), but it's consistent with the TRM
Ground Water Source HP | HSPF | COP
-System subtype- | Select System Type
water to air | 12.6244 | 3.7 |  | Incomplete Inputs
water to water | 10.5772 | 3.1
Ground Source HP | HSPF | COP
-System subtype- | Select System Type
Water to air | 14.6716 | 4.3
Brine to air | 10.9184 | 3.2
Water to water | 12.6244 | 3.7
Brine to water | 8.53 | 2.5
Electric Resistance | 3.412
Gas Heating inputs
I tried doing all heating inputs in one input box, but it was more confusing than helpful
Chosen system type | -Existing Gas System Type-
Chosen system sub type | -System Subtype-
CapacityHeat | 0
EFGasBase | #N/A
-Existing Gas System Type-
Not Needed
Not Needed |  |  |  | boiler System Subtype options
Not Needed |  |  |  | <300,000 Btu/h
Not Needed |  |  |  | 300,000-2,500,000 Btu/h
Not Needed |  |  |  | >2,500,000 Btu/h
Not Needed
Not Needed |  |  |  | furnace system subtype options
<225,000 Btu/h
>=225,000 Btu/h
-System Subtype- |  |  |  | --
Incomplete Inputs
Incomplete Inputs
Incomplete Inputs
Hgrid
Hours of operation are not clearly defined by the TRM - to be conservative, we will add the heating and cooling EFLH values to get a total full load hour runtime. This could possibly be improved by backing out actual runtime from the EFLH development methodology
Heating EFLH | Incomplete |  |  |  | 6% | This is a variable for the tool user/designer. Line losses are not likely to be known project-to-project either. We will use a conservative value as a default and the tool user can adjust the value here, if known
Cooling EFLH | Incomplete
Total operating hours | #VALUE!
Line losses value | 6%
intermediate Hgrid value | #VALUE! |  |  |  | operating hours | intermediate Hgrid value
Hgrid | #VALUE! |  |  |  | 0 | 9968
[5 empty] | 6500 | 9996
Heat rate of the grid in btu/kWh based on the average fossil heat rate for the EPA eGRID subregion and includes a factor that takes into account T&D losses.
For systems operating less than 6,500 hrs per year:
Use the Non-baseload heat rate provided by EPA eGRID for RFC West region for ComEd territory (including independent providers connected to RFC West), and SERC Midwest region for Ameren territory (including independent providers connected to SERC Midwest) 740. Also include any line losses.
For systems operating more than 6,500 hrs per year:
Use the All Fossil Average heat rate provided by EPA eGRID for RFC West region for ComEd territory, and SERC Midwest region for Ameren territory. Also include any line losses
From TRM footnote 740 (in version 8) |  |  |  | - Non-Baseload RFC West: 10,539 Btu/kWh * (1 + Line Losses)
|  |  | For systems operating < 6500 hours per year in Ameren territory: | - Non-Baseload SERC Midwest: 9,968 Btu/kWh * (1 + Line Losses)
- All Fossil Average RFC West: 9,962 Btu/kWh * (1 + Line Losses)
|  |  | For systems operating > 6500 hours per year in Ameren territory: | - All Fossil Average SERC Midwest: 9,996 Btu/kWh * (1 + Line Losses)
Input completeness
Complete - All required inputs have been entered
Incomplete - Required inputs still needed
Not Needed - Not Applicable to this project
Incentive

## electric calculations (hidden)
Variable required for the calc? Depends on Use Case
Input required? | variable | value | default value | units | definition | New construction, non-fuel switch | Time of Sale, non-fuel switch | Early Replacement, non-fuel switch | Early Replacement, fuel switch | New construction, fuel switch | Time of Sale, fuel switch
No | Capacitycool | 0 | Required Input | (Btu/hr) | Cooling Capacity of Ground Source Heat Pump. Actual installed | Y | Y | Y | Y | Y | Y
No | EFLHCool | Incomplete | Incomplete | (hours) | Cooling Equivalent Full Load Hours. Dependent on building type, provided in section 4.4 HVAC End Use | Y | Y | Y | Y | Y | Y
No | EERExist | 0 | Required Input | (kBtu/hr / kW) | Energy Efficiency Ratio (EER) of existing cooling unit. In (kBtu/hr/kW). Use actual EER rating where it is possible to measure or reasonably estimate. If it is not possible to estimate existing unit efficiency, change project to Time-of-Sale. If EER unknown but SEER is available, convert using the tool to the right* | N | N | Y | Y | N | N
No | EERbase | Incomplete | Incomplete | (kBtu/hr / kW) | Energy Efficiency Ratio (EER) of baseline replacement cooling system. Use minimum standard efficiencies as specified in tables in ‘Definition of Baseline Equipment’ section | Y | Y | Y | Y | Y | Y
No | EERGSHP | 0 | Required Input | (kBtu/hr / kW) | Part Load Energy Efficiency Ratio efficiency of efficient GSHP unit. Actual installed | Y | Y | Y | Y | Y | Y
No | ElecHeat | Incomplete | Incomplete | flag | 1 if baseline/existing heating system is electric. 0 if existing system is non electric | Y | Y | Y | Y | Y | Y
No | CapacityHeat | 0 | Required Input | (Btu/hr) | Heating Capacity of Ground Source Heat Pump. Actual installed | Y | Y | Y | Y | Y | Y
No | EFLHHeat | Incomplete | Incomplete | (hours) | Heating Equivalent Full Load Hours. Dependent on building type, provided in section 4.4 HVAC End Use | Y | Y | Y | Y | Y | Y
No | HSPFExist | 0 | Required Input | (kBtu/kWh) | HSFPExist is the actual Heating System Performance Factor of existing electric heating system in (kBtu/kWh). If it is not possible to estimate, change to use Time of Use assumptions. (for electric resistance, HSPFexist is 3.14) | N | N | Y | N | N | N
No | HSPFbase | Incomplete Inputs | Incomplete Inputs | (kBtu/kWh) | Heating System Performance Factor of new replacement baseline heating system [of the existing type, but new] | Y | Y | Y | N | N | N
No | HSPFASHP | Input CapacityHeat | Input CapacityHeat | (kBtu/kWh) | Heating System Performance Factor of new replacement ASHP. (for fuel switch). Refer to applicable Table in ‘Definition of Baseline Equipment’ section | N | N | N | Y | Y | Y
No | COPGSHP | 0 | Required Input | (unitless) | Part Load Coefficient of Performance of efficient GSHP. Actual installed | Y | Y | Y | Y | Y | Y
No | Constant | 3.412 | 3.412 | (kWh/kbtu) | Constant to convert the COP of the unit to the Heating Season Performance Factor (HSPF) | Y | Y | Y | Y | Y | Y
No | ElecDHW | 0 | Tool incomplete | flag | 1 if building has electric DHW. 0 if building has non electric DHW. 0 if one to one replacement of existing Ground Source Heat Pump | Y | Y | Y | Y | Y | Y
No | %DHW | 0 | Tool incomplete | (%) | Percentage of total DHW load that the GSHP will provide. Actual if known. If unknown and if desuperheater installed assume 44%. 0% if no desuperheater installed | Y | Y | Y | Y | Y | Y
No | Efelecbase | 0 | Tool incomplete |  | Energy Factor of baseline electric DHW. Actual. If unknown or for new construction assume federal standard as defined in applicable table in ‘Definition of Baseline Equipment’ section | Y | Y | Y | Y | Y | Y
No | HotWaterUseGallon | 0 | Tool incomplete | oof. Yeesh. Separate sub input routine required |  | Y | Y | Y | Y | Y | Y
No | γWater | 8.33 | 8.33 | (lb/gal) | Density of water. 8.33 pounds per gallon | Y | Y | Y | Y | Y | Y
No | Tout | 125 | 125 | (°F) | Tank temperature. 125°F | Y | Y | Y | Y | Y | Y
No | Tin | 54 | 54 | (°F) | Incoming water temperature from well or municiplal system. 54°F | Y | Y | Y | Y | Y | Y
No | Constant | 1 | 1 | (Btu/lb*°F) | Heat Capacity of water | Y | Y | Y | Y | Y | Y
No | Constant | 3412 | 3412 | (kWh/btu) | Conversion from Btu to kWh | Y | Y | Y | Y | Y | Y
This is 3.412 in the variable definition, but 3412 in the algorithms. Pretty sure it should be 3412, but maybe verify
Building Type |  |  |  |  | * If EER unknown but SEER is available, convert using the equation: EERexist = (-0.02 * SEERexist^2) + (1.12 * SEERexist). If it is not possible to estimate existing unit efficiency, change project to Time-of-Sale
Climate Zone
Use cases:
New construction, non-fuel switch
Time of Sale, non-fuel switch
ΔkWh = [Cooling savings] + [Heating savings] + [DHW savings]
Cooling Savings = (Capacitycool * EFLHCool * (1/EERbase – 1/EERGSHP))/1000
Heating Savings = ElecHeat *((CapacityHeat * EFLHHeat * (1/HSPFbase – 1/(COPGSHP * 3.412)))/1000)
DHW Savings = ElecDHW * (%DHW * ((1/EFelecbase) * HotWaterUseGallon * γWater * (Tout – Tin) * 1/3412))
0 | [Cooling savings] | Years 1-25
0 | [Heating savings] | Years 1-25
0 | [DHW savings] | Years 1-25
0 | ΔkWh | Years 1-25
Not Applicable | Not Applicable | Not Applicable
Not Applicable | Not Applicable | Not Applicable
Not Applicable | Not Applicable | Not Applicable
Not Applicable | Not Applicable | Not Applicable
Use cases:
New construction, fuel switch
Time of Sale, fuel switch
ΔkWh = [Cooling savings] + [Heating savings from base ASHP to GSHP] + [DHW savings]
Cooling Savings = (Capacitycool * EFLHCool * (1/EERbase - 1/EERGSHP))/1000
Heating Savings from base ASHP to GSHP = (CapacityHeat * EFLHHeat * (1/HSPFASHP - 1/(COPGSHP * 3.412)))/1000
DHW Savings = ElecDHW * (%DHW * ((1/EFelecbase) * HotWaterUseGallon * γWater * (Tout - Tin) * 1 /3412))
0 | [Cooling savings] | Years 1-25
0 | [Heating Savings from base ASHP to GSHP] | Years 1-25
0 | [DHW savings] | Years 1-25
0 | ΔkWh | Years 1-25
Not Applicable | Not Applicable | Not Applicable
Not Applicable | Not Applicable | Not Applicable
Not Applicable | Not Applicable | Not Applicable
Not Applicable | Not Applicable | Not Applicable
Use cases:
Early Replacement, non-fuel switch
ΔkWh for remaining life of existing unit (1st 8 years): = [Cooling savings] + [Heating savings] + [DHW savings]
Cooling Savings = (Capacitycool * EFLHCool * (1/EERExist – 1/EERGSHP))/1000
Heating Savings = ElecHeat *((CapacityHeat * EFLHHeat * (1/HSPFexist – 1/(COPGSHP * 3.412)))/1000)
DHW Savings = ElecDHW * (%DHW * ((1/EFelecbase) * HotWaterUseGallon * γWater * (Tout – Tin) * 1/3412))
ΔkWh for remaining measure life (next 17 years): = [Cooling savings] + [Heating savings ] + [DHW savings]
Cooling Savings = (Capacitycool * EFLHCool * (1/EERbase – 1/EERGSHP))/1000
Heating Savings = ElecHeat *((CapacityHeat * EFLHHeat * (1/HSPFBase – 1/(COPGSHP * 3.412)))/1000)
DHW Savings = ElecDHW * (%DHW * ((1/ EFelecbase) * HotWaterUseGallon * γWater * (Tout – Tin) * 1 /3412))
0 | [Cooling savings] | Years 1-8 |  | Cooling Savings = (Capacitycool * EFLHCool * (1/EERExist – 1/EERGSHP))/1000
0 | [Heating savings] | Years 1-8 |  | Heating Savings from base ASHP to GSHP = (CapacityHeat * EFLHHeat * (1/HSPFASHP – 1/(COPGSHP * 3.412)))/1000
0 | [DHW savings] | Years 1-8 |  | DHW Savings = ElecDHW * (%DHW * ((1/ EFelecbase) * HotWaterUseGallon * γWater * (Tout – Tin) * 1 /3412))
0 | ΔkWh | Years 1-8
0 | [Cooling savings] | Years 9-25
0 | [Heating savings] | Years 9-25
0 | [DHW savings] | Years 9-25
0 | ΔkWh | Years 9-25
Use cases:
Early Replacement, fuel switch
ΔkWh for remaining life of existing unit (1st 8 years): = [Cooling savings] + [Heating savings from base ASHP to GSHP] + [DHW savings]
Cooling Savings = (Capacitycool * EFLHCool * (1/EERExist – 1/EERGSHP))/1000
Heating Savings from base ASHP to GSHP = (CapacityHeat * EFLHHeat * (1/HSPFASHP – 1/(COPGSHP * 3.412)))/1000
DHW Savings = ElecDHW * (%DHW * ((1/ EFelecbase) * HotWaterUseGallon * γWater * (Tout – Tin) * 1 /3412))
ΔkWh for remaining measure life (next 17 years): = [Cooling savings] + [Heating savings from base ASHP to GSHP] + [DHW savings]
Cooling Savings = (Capacitycool * EFLHCool * (1/EERbase – 1/EERGSHP))/1000
Heating Savings from base ASHP to GSHP = (CapacityHeat * EFLHHeat * (1/HSPFASHP – 1/(COPGSHP * 3.412)))/1000
DHW Savings = ElecDHW * (%DHW * ((1/ EFelecbase) * HotWaterUseGallon * γWater * (Tout – Tin) * 1 /3412))
0 | [Cooling savings] | Years 1-8
0 | [Heating savings from base ASHP to GSHP] | Years 1-8
0 | [DHW savings] | Years 1-8
0 | ΔkWh | Years 1-8
0 | [Cooling savings] | Years 9-25
0 | [Heating savings from base ASHP to GSHP] | Years 9-25
0 | [DHW savings] | Years 9-25
0 | ΔkWh | Years 9-25
Final savings
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete

## gas calculations (hidden)
Variable required for the calc? Depends on Use Case
Input required? | variable | value | default value | units | definition | New construction, non-fuel switch | Time of Sale, non-fuel switch | Early Replacement, non-fuel switch | Early Replacement, fuel switch | New construction, fuel switch | Time of Sale, fuel switch
No | ElecHeat | Incomplete | Incomplete | flag | 1 if existing heating system is electric. 0 if existing system is non electric | Y | Y | Y | Y | Y | Y
No | CapacityHeat | 0 | Required Input | (Btu/hr) | Heating Capacity of Ground Source Heat Pump. Actual installed | Y | Y | Y | Y | Y | Y
No | EFLHHeat | Incomplete | Incomplete | (hours) | Heating Equivalent Full Load Hours. Dependent on building type, provided in section 4.4 HVAC End Use | Y | Y | Y | Y | Y | Y
No | HSPFASHP | Input CapacityHeat | Input CapacityHeat | (kBtu/kWh) | Heating System Performance Factor of new replacement ASHP. (for fuel switch). Refer to applicable Table in ‘Definition of Baseline Equipment’ section | N | N | N | Y | Y | Y
No | Constant | 3.412 | 3.412 | (kWh/btu) | Constant to convert the COP of the unit to the Heating Season Performance Factor (HSPF) | Y | Y | Y | Y | Y | Y
No | ElecDHW | 0 | Tool incomplete | flag | 1 if building has electric DHW. 0 if building has non electric DHW. 0 if one to one replacement of existing Ground Source Heat Pump | Y | Y | Y | Y | Y | Y
No | %DHW | 0 | Tool incomplete | (%) | Percentage of total DHW load that the GSHP will provide. Actual if known. If unknown and if desuperheater installed assume 44%. 0% if no desuperheater installed | Y | Y | Y | Y | Y | Y
No | HotWaterUseGallon | 0 | Tool incomplete | oof. Yeesh. Separate sub input routine required |  | Y | Y | Y | Y | Y | Y
No | γWater | 8.33 | 8.33 | (lb/gal) | Density of water. 8.33 pounds per gallon | Y | Y | Y | Y | Y | Y |  |  | 100000
No | Tout | 125 | 125 | (°F) | Tank temperature. 125°F | Y | Y | Y | Y | Y | Y
No | Tin | 54 | 54 | (°F) | Incoming water temperature from well or municiplal system. 54°F | Y | Y | Y | Y | Y | Y
No | Constant | 1 | 1 | (Btu/lb*°F) | Heat Capacity of water | Y | Y | Y | Y | Y | Y
No | Constant | 3412 | 3412 | (kWh/btu) | Conversion from Btu to kWh | Y | Y | Y | Y | Y | Y | variables above this line are common to electric calcs
No | Gas_Heating_Load | Incomplete | Incomplete | therms | Estimate of annual heating load = Capacityheat * EFLHheat / 100,000 | N | N | N | Y | Y | Y
No | Hgrid | Incomplete | Incomplete | btu/kWh | Heat rate of the grid in btu/kWh… full description in TRM | N | N | N | Y | Y | Y
No | GasEffbase | Incomplete | Incomplete | % | Minimum federal standard baseline efficiency of boiler or furnace | N | N | N | Y | Y | Y |  | in output btu/input btu
No | kWhtoTherm | Incomplete | Incomplete | Therm/kWh | Converts source kWh to Therms | N | N | N | Y | Y | Y
No | EFGasBase |  |  |  | Energy factor of Baseline natural gas DHW heater
No | GasEffExist | 0% | Required Input | % | GasEffExist is the actual efficiency of existing gas boiler or furnace as a percentage (output btu/input btu - AFUE or Ef). If it is not possible to estimate, change to use Time of Use assumptions. | N | N | N | Y | N | N
This is 3.412 in one place in the TRM and 3412 in another - verify which it should be
Building Type |  |  |  |  | * If EER unknown but SEER is available, convert using the equation: EERexist = (-0.02 * SEERexist^2) + (1.12 * SEERexist). If it is not possible to estimate existing unit efficiency, change project to Time-of-Sale
Climate Zone
Use cases: | [5 empty] | All savings calcs are for both electric and gas utility type (Ameren). Gas-only would use different calcs
New construction, non-fuel switch
Time of Sale, non-fuel switch
Early Replacement, non-fuel switch
ΔTherms = 0
0 | [Heating savings] | Years 1-25
0 | [DHW savings] | Years 1-25
0 | ΔTherms | Years 1-25
Not Applicable | Not Applicable | Not Applicable
Not Applicable | Not Applicable | Not Applicable
Not Applicable | Not Applicable | Not Applicable
Use cases:
New construction, fuel switch
Time of Sale, fuel switch
ΔTherms = [Heating Savings] + [DHW Savings]
Heating Savings = Replaced baseline gas consumption – therm equivalent of base ASHP source kWh
= (1 – ElecHeat) * ((Gas_Heating_Load/GasEffbase) – (kWhtoTherm * EFLHheat * Capacityheat * 1/HSPFASHP)/1000)
DHW Savings = (1 – ElecDHW) * (%DHW * (1/ EFGasBase * HotWaterUseGallon * γWater * (TOUT – TIN) * 1.0) / 100,000)
For TOS and NC, I'm assuming the efficiency rating of the gas system is based on the type of existing system of the same capacity of the new system. For ER, I'm assuming the efficiency rating of the gas system is based on the type and capacity of the existing system
0 | [Heating savings from base ASHP to GSHP] | Years 1-25
0 | [DHW savings] | Years 1-25
0 | ΔTherms | Years 1-25
Not Applicable | Not Applicable | Not Applicable
Not Applicable | Not Applicable | Not Applicable
Not Applicable | Not Applicable | Not Applicable
Use cases:
Early Replacement, fuel switch
ΔTherms for remaining life of existing unit (1st 8 years):
= [Heating Savings] + [DHW Savings]
Heating Savings = Replaced existing gas consumption – therm equivalent of base ASHP source kWh
= (1 – ElecHeat) * ((Gas_Heating_Load/GasEffExist) – (kWhtoTherm * EFLHheat * Capacityheat * 1/HSPFASHP)/1000)
DHW Savings = (1 – ElecDHW) * (%DHW * (1/ EFGasBase * HotWaterUseGallon * γWater * (TOUT – TIN) * 1.0) / 100,000)
ΔTherms for remaining measure life (next 17 years):
= [Heating Savings] + [DHW Savings]
Heating Savings = Replaced baseline gas consumption – therm equivalent of base ASHP source kWh
= (1 – ElecHeat) * ((Gas_Heating_Load/GasEffBase) – (kWhtoTherm * EFLHheat * Capacityheat * 1/HSPFASHP)/1000)
DHW Savings = (1 – ElecDHW) * (%DHW * (1/ EFGasBase * HotWaterUseGallon * γWater * (TOUT – TIN) * 1.0) / 100,000)
0 | [Heating savings from equivalent existing ASHP to GSHP] | Years 1-8
| [DHW savings] | Years 1-8
0 | ΔTherms | Years 1-8
0 | [Heating savings from base ASHP to GSHP] | Years 9-25
| [DHW savings] | Years 9-25
0 | ΔTherms | Years 9-25
Final savings
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete
Incomplete | Incomplete | Incomplete

## Tables (hidden)
Program Type | -Choose One-
Climate Zone | -Climate Zone-
Building Type | -Choose One-
Existing or new | Incomplete
Simplified Zone | Incomplete
Heating EFLH | Incomplete
Cooling EFLH | Incomplete
Select Program Type First
Building Type | Heating EFLH Existing Buildings |  |  |  |  | Cooling EFLH Existing Buildings
| Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion)
-Choose One- | Select Building Type | Select Building Type | Select Building Type | Select Building Type | Select Building Type | Select Building Type | Select Building Type | Select Building Type | Select Building Type | Select Building Type
Assembly | 1787 | 1831 | 1635 | 1089 | 1669 | 725 | 796 | 937 | 1183 | 932
Assisted Living | 1683 | 1646 | 1446 | 1063 | 1277 | 1475 | 1457 | 1773 | 2110 | 1811
Auto Dealership | 2981 | 2950 | 2694 | 2368 | 2437 | 996 | 1051 | 1343 | 1582 | 1414
College | 1256 | 1293 | 1138 | 1116 | 1131 | 572 | 564 | 676 | 776 | 613
Convenience Store | 1481 | 1368 | 1214 | 871 | 973 | 1088 | 1067 | 1368 | 1541 | 1371
Drug Store | 2848 | 2947 | 2568 | 2362 | 2516 | 858 | 943 | 1133 | 1279 | 1092
Elementary School | 1614 | 1603 | 1409 | 1209 | 1269 | 834 | 837 | 999 | 1264 | 967
Garage | 985 | 969 | 852 | 680 | 752 | 934 | 974 | 1226 | 1582 | 1383
Grocery | 1467 | 1551 | 1364 | 1367 | 1375 | 826 | 914 | 1151 | 1329 | 1240
Healthcare Clinic | 1446 | 1526 | 1452 | 1553 | 1574 | 1220 | 1294 | 1505 | 1658 | 1534
High School | 1807 | 1855 | 1649 | 1591 | 1622 | 892 | 883 | 1066 | 1397 | 1018
Hospital - CAV no econ | 1216 | 1220 | 1072 | 1001 | 1028 | 1719 | 1799 | 2068 | 2238 | 2066
Hospital - CAV econ | 1387 | 1398 | 1252 | 1222 | 1269 | 1267 | 1302 | 1604 | 1798 | 1592
Hospital - VAV econ | 665 | 697 | 628 | 646 | 615 | 3313 | 3332 | 3458 | 3546 | 3311
Hospital - FCU | 1622 | 1571 | 1374 | 1220 | 1281 | 1575 | 1562 | 1921 | 1979 | 1812
Hotel/Motel | 1597 | 1634 | 1468 | 1376 | 1451 | 1106 | 1148 | 1453 | 1605 | 1435
Hotel/Motel - Common | 1670 | 1733 | 1549 | 1496 | 1557 | 1108 | 1168 | 1430 | 1574 | 1406
Hotel/Motel - Guest | 1555 | 1597 | 1433 | 1316 | 1400 | 1061 | 1106 | 1391 | 1509 | 1401
Manufacturing Facility | 1048 | 1013 | 939 | 567 | 634 | 1010 | 1055 | 1209 | 1453 | 1273
MF - High Rise | 1565 | 1540 | 1448 | 1089 | 1125 | 928 | 920 | 1059 | 1360 | 1205
MF - High Rise - Common | 537 | 558 | 501 | 480 | 499 | 1405 | 1383 | 1479 | 1527 | 1466
MF - High Rise - Residential | 1665 | 1666 | 1512 | 1145 | 1207 | 764 | 807 | 976 | 1216 | 1147
MF - Mid Rise | 1730 | 1782 | 1589 | 1538 | 1560 | 787 | 855 | 1099 | 1198 | 1082
Movie Theater | 1916 | 1905 | 1718 | 1288 | 1538 | 876 | 745 | 1036 | 1178 | 1010
Office - High Rise - CAV no econ | 995 | 1036 | 933 | 786 | 832 | 1357 | 1404 | 1587 | 1753 | 1468
Office - High Rise - CAV econ | 2244 | 2237 | 2024 | 1553 | 1608 | 3489 | 3453 | 3663 | 4403 | 4208
Office - High Rise - VAV econ | 1552 | 1432 | 1239 | 1077 | 1098 | 847 | 887 | 991 | 1092 | 893
Office - High Rise - FCU | 1015 | 993 | 899 | 773 | 809 | 1083 | 1116 | 1269 | 1348 | 1266
Office - Low Rise | 2825 | 2625 | 2365 | 2007 | 2040 | 1796 | 1790 | 2233 | 2342 | 2219
Office - Mid Rise | 1672 | 1629 | 1454 | 1356 | 1399 | 1128 | 1153 | 1360 | 1461 | 1356
Public Sector | 2757 | 2670 | 2383 | 2149 | 2186 | 2983 | 3009 | 3762 | 4030 | 3740
Religious Building | 1603 | 1504 | 1440 | 1054 | 1205 | 861 | 817 | 967 | 1159 | 1067
Restaurant | 1326 | 1328 | 1179 | 1091 | 1122 | 990 | 1021 | 1273 | 1411 | 1290
Retail - Department Store | 1365 | 1322 | 1193 | 1034 | 1088 | 639 | 640 | 775 | 936 | 812
Retail - Strip Mall | 1347 | 1325 | 1183 | 1064 | 1096 | 697 | 720 | 915 | 998 | 930
Warehouse | 1285 | 1286 | 1180 | 1147 | 1224 | 252 | 265 | 363 | 377 | 379
Unknown | 1709 | 1678 | 1508 | 1287 | 1411 | 1003 | 1019 | 1230 | 1403 | 1236
Heating and cooling building types for new construction don't quite match. There is no Office - High Rise - CAV econ for heating, so I removed it for cooling too
Building Type | Heating EFLH New Construction |  |  |  |  | Cooling EFLH New Construction
| Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion)
-Choose One- | Select Building Type | Select Building Type | Select Building Type | Select Building Type | Select Building Type | Select Building Type | Select Building Type | Select Building Type | Select Building Type | Select Building Type
Auto Dealership | 1286 | 1185 | 1279 | 1138 | 1078 | 806 | 923 | 792 | 938 | 1028
College | 942 | 834 | 906 | 831 | 818 | 925 | 990 | 994 | 1156 | 1217
Drug Store | 1023 | 930 | 1017 | 889 | 822 | 813 | 931 | 744 | 836 | 1083
Elementary School | 949 | 878 | 943 | 861 | 859 | 724 | 821 | 732 | 753 | 999
Grocery | 2795 | 2788 | 2549 | 2380 | 2597 | 643 | 568 | 569 | 562 | 511
Healthcare Clinic | 1534 | 1417 | 1555 | 1395 | 1371 | 1964 | 2093 | 1932 | 2055 | 2221
High School | 1502 | 1549 | 1368 | 1283 | 1299 | 1807 | 1642 | 2093 | 2292 | 1830
Hospital - CAV no econ | 2345 | 2207 | 2318 | 2110 | 2195 | 2627 | 2751 | 2662 | 2782 | 2962
Hospital - CAV econ | 2345 | 2207 | 2318 | 2110 | 2195 | 2627 | 2751 | 2662 | 2782 | 2962
Hospital - VAV econ | 2345 | 2207 | 2318 | 2110 | 2195 | 2627 | 2751 | 2662 | 2782 | 2962
Hospital - FCU | 2345 | 2207 | 2318 | 2110 | 2195 | 2627 | 2751 | 2662 | 2782 | 2962
Hotel/Motel - Residential | 1412 | 1243 | 1439 | 1405 | 1146 | 1639 | 1836 | 1712 | 1851 | 1983
Hotel_Motel_Common | 1554 | 1415 | 1519 | 1410 | 1361 | 2343 | 2472 | 2286 | 2400 | 2590
Hotel_Motel_Guest | 1538 | 1083 | 1554 | 1381 | 987 | 788 | 1024 | 846 | 1073 | 1164
MF - High Rise | 1308 | 884 | 1361 | 1125 | 865 | 1338 | 1705 | 1287 | 1500 | 1932
MF - High Rise - Common | 1581 | 1280 | 1590 | 1349 | 1220 | 773 | 912 | 751 | 878 | 972
MF - High Rise - Residential | 1352 | 946 | 1413 | 1174 | 917 | 1299 | 1663 | 1245 | 1451 | 1882
MF - Mid Rise | 1637 | 1385 | 1637 | 1434 | 1322 | 1341 | 1633 | 1245 | 1492 | 1818
Office - High Rise - FCU | 987 | 870 | 1001 | 893 | 837 | 1296 | 1465 | 1281 | 1477 | 1574
Office - High Rise - VAV econ | 987 | 870 | 1001 | 893 | 837 | 1296 | 1465 | 1281 | 1477 | 1574
Office - Mid Rise | 867 | 759 | 892 | 792 | 701 | 957 | 1149 | 958 | 1122 | 1270
Office - High Rise - CAV no econ | 967 | 854 | 971 | 876 | 804 | 1433 | 1644 | 1411 | 1632 | 1793
Office Low Rise | 954 | 916 | 826 | 667 | 664 | 947 | 989 | 1090 | 1302 | 1076
Public Sector | 480 | 352 | 501 | 407 | 347 | 379 | 429 | 371 | 423 | 576
Restaurant | 787 | 797 | 671 | 811 | 820 | 768 | 761 | 1034 | 1110 | 994
Retail - Department Store | 1286 | 1185 | 1279 | 1138 | 1078 | 806 | 924 | 796 | 939 | 1027
Retail - Strip Mall | 973 | 867 | 972 | 857 | 777 | 722 | 789 | 667 | 834 | 911
Warehouse | 1413 | 1390 | 1398 | 1298 | 1290 | 389 | 522 | 408 | 527 | 567
Unknown | 1133 | 1064 | 1091 | 982 | 960 | 984 | 1045 | 1047 | 1177 | 1176
Table2: IECC 2015 ASHP Minimum Efficiency Requirements (effective 1/1/2016 to 3/30/2019): | [6 empty] | Not used. Program after 3/30/2019
Table 3: IECC 2015 Electric Chillers, Air-Cooled and Water-Cooled minimum efficiencies (effective 1/1/2016 to 3/30/2019) | [6 empty] | Not used. Program after 3/30/2019
Table 4: IECC 2015 Boiler minimum efficiency requirements (effective 1/1/2016 to 3/30/2019) | [6 empty] | Not used. Program after 3/30/2019
Table 5: IECC 2015 Warm-air Furnace minimum efficiency standards (effective 1/1/2016 to 3/30/2019) | [6 empty] | Not used. Program after 3/30/2019
Table 6: IECC 2015 Water Heaters mininmum performance (effective 1/1/2016 to 3/30/2019) | [6 empty] | Not used. Program after 3/30/2019
Table7: IECC 2018 ASHP Minimum Efficiency Requirements (effective 7/1/2019) | [6 empty] | Table 7
[7 empty] | Ground water source | water to air | <135kBtuh | 18 | EER
[8 empty] | water to water | <135kBtuh | 16.3 | EER
[7 empty] | Ground source | water to air | <17kBtuh | 12.2 | EER
[9 empty] | 17-65kbtuh | 13 | EER
[9 empty] | 65-135kBtuh | 13 | EER
[8 empty] | brine to air | <135kBtuh | 14.1 | EER
[8 empty] | water to water | <135kBtuh | 10.6 | EER
[8 empty] | brine to water | <135kBtuh | 12.1 | EER
Table 7 continued: | [6 empty] | Air Source Heat Pump
[7 empty] | Air cooled (heating mode) | Split | <65kBtuh | 8.2 | HSPF
[7 empty] | Air cooled (heating mode) | Single | <65kBtuh | 8 | HSPF
[7 empty] | Through-the-wall (heating mode) | Split | <30kBtuh | 7.4 | HSPF | -choose rating test type-
[7 empty] | Through-the-wall (heating mode) | single | <30kBtuh | 7.4 | HSPF | 47F db/43F wb outdoor air
[7 empty] | Small-duct high velocity (heating mode) |  | <65kBtuh | 6.8 | HSPF | 17F db/15F wb outdoor air
[7 empty] | Air cooled (heating mode) | 47F db/43F wb outdoor air | 65-135kBtuh | 3.3 | COP
[7 empty] | Air cooled (heating mode) | 17F db/15F wb outdoor air | 65-135kBtuh | 2.25 | COP
[7 empty] | Air cooled (heating mode) | 47F db/43F wb outdoor air | >135kBtuh | 3.2 | COP
[7 empty] | Air cooled (heating mode) | 17F db/15F wb outdoor air | >135kBtuh | 2.05 | COP
[7 empty] | Ground water source | water to air | <135kBtuh | 3.7 | COP
[8 empty] | water to water | <135kBtuh | 3.1 | COP
[7 empty] | Ground source | water to air | <17kBtuh | 4.3 | COP
[8 empty] | brine to air | <135kBtuh | 3.2 | COP
[8 empty] | water to water | <135kBtuh | 3.7 | COP
[8 empty] | brine to water | <135kBtuh | 2.5 | COP
Table 8: IECC 2018 Electric Chillers, Air-Cooled and Water-Cooled minimum efficiencies (effective 7/1/2019)
Chiller EER ratings
[8 empty] | Path A FL | Path A IPLV | Path B FL | Path B IPLV |  | chosen path
[8 empty] | 2 | 3 | 4 | 5 |  | Path B IPLV
[7 empty] | Air cooled <150 tons | 10.1 | 13.7 | 9.7 | 15.8 |  | 5 | column to to reference in VLOOKUP
[7 empty] | Air cooled 150+ tons | 10.1 | 14 | 9.7 | 16.1
12 divided by kW/ton equals EER in Btu/W. is that legit?
[7 empty] | Water cooled, PD <75 tons | 16 | 17.3913 | 15.3846 | 24 |  | 0.75 | 0.69 | 0.78 | 0.5
[7 empty] | Water cooled, PD 75-150 tons | 16.6667 | 21.4286 | 16 | 24.4898 |  | 0.72 | 0.56 | 0.75 | 0.49
[7 empty] | Water cooled, PD 150-300 tons | 18.1818 | 22.2222 | 17.6471 | 27.2727 |  | 0.66 | 0.54 | 0.68 | 0.44
[7 empty] | Water cooled, PD 300-600 tons | 19.6721 | 23.0769 | 19.2 | 29.2683 |  | 0.61 | 0.52 | 0.625 | 0.41
[7 empty] | Water cooled, PD 600+ tons | 21.4286 | 24 | 20.5128 | 31.5789 |  | 0.56 | 0.5 | 0.585 | 0.38
[7 empty] | Water cooled, cetrifugal <150 tons | 19.6721 | 21.8182 | 17.2662 | 27.2727 |  | 0.61 | 0.55 | 0.695 | 0.44
[7 empty] | Water cooled, cetrifugal 150-300 tons | 19.6721 | 21.8182 | 18.8976 | 30 |  | 0.61 | 0.55 | 0.635 | 0.4
[7 empty] | Water cooled, cetrifugal 300-400 tons | 21.4286 | 23.0769 | 20.1681 | 30.7692 |  | 0.56 | 0.52 | 0.595 | 0.39
[7 empty] | Water cooled, cetrifugal 400-600 tons | 21.4286 | 24 | 20.5128 | 31.5789 |  | 0.56 | 0.5 | 0.585 | 0.38
[7 empty] | Water cooled, cetrifugal 600+ tons | 21.4286 | 24 | 20.5128 | 31.5789 |  | 0.56 | 0.5 | 0.585 | 0.38
Table 9: IECC 2018 Boiler minimum efficiency requirements (effective 7/1/2019)
[13 empty] | #N/A | column to to reference in VLOOKUP
[8 empty] | 2 | 3 | 4
[7 empty] | Hot Water Boiler - gas-fired | 82% | 80% | 82% |  | <300,000 Btu/h | 2
[7 empty] | Hot Water Boiler - oil-fired | 84% | 82% | 84% |  | 300,000-2,500,000 Btu/h | 3
[7 empty] | Steam Boiler - gas-fired | 80% |  |  |  | >2,500,000 Btu/h | 4
[7 empty] | Steam Boiler - oil-fired | 82% | 81% | 81%
[7 empty] | Warm Air Furnace - gas-fired | 80% | 80% |  |  | <225,000 Btu/h | 2
[7 empty] | Warm Air Furnace - oil-fired | 83% | 81% |  |  | >=225,000 Btu/h | 3
[7 empty] | Warm Air Unit Heater | 80% | 80%
Table 10: IECC 2018 Warm-air Furnace minimum efficiency standards (effective 7/1/2019)
Table 11: IECC 2018 Water Heaters mininmum performance (effective 7/1/2019)